## Part 1
Date
Number
Design verification part 1
Project: SPEP 185mm Nr. *************
Distribution board:NSHV **********
Assembly manufacturer
Project: SPEP 185mm Nr. *************
Distribution board:NSHV **********
Cabinet system: System pro E power
Low voltage switchgear and controlgear assembly
Power switchgear and controlgear assemblies (PSC) - Design verification according to IEC EN 61439-2
Nominal values of the Assembly
Rated voltage: |  | V AC |  |  | Short circuit withstand strength
Rated frequency: |  | Hz |  |  | Icc: | kA
Electrical system: |  |  |  |  | Icw: | kA
Rated current of the Assembly InA: |  |  |  | A | Ipk: | kA
Rated insulation voltage (Ui): |  |  |  | V
Rated impulse withstand voltage (Uimp): |  |  |  | kV
Design verification provided for (see part 2)
0
Design verification carried:
(Place / Date) |  |  | (Name and Signature)
(Place / Date) |  |  | (Name and Signature)
Company stamp

## Part 2
Design verification part 2
Par. | Characteristic to be verified | Verification through | Notes
10.2.2 | Resistance to corrosion | ABB
10.2.3.1 | Verification of thermal stability of enclosures | Not required | Steel sheet enclosure.
10.2.3.2 | Verification of resistance of insulating materials to abnormal heat and fire due to internal electric effects | ABB
10.2.4 | Resistance to ultra-violet (UV) radiation | Not required
10.2.5 | Lifting | ABB
10.2.6 | Mechanical impact | ABB
10.2.7 | Marking | ASSEMBLY manufacturer | The ASSEMBLY manufacturer shall provide each ASSEMBLY with one or more labels, marked in a durable manner and located in a place such that they are visible and legible when the ASSEMBLY is installed and in operation. Compliance is checked according to the test of 10.2.7 and by inspection.
10.3 | Degree of protection of ASSEMBLIES | ABB
10.4 | Clearances and creepage distances | ABB
10.5.2 | Effective earth continuity between the exposed conductive parts of the ASSEMBLY and the protective circuit | ABB
10.5.3 | Short-circuit withstand strength of the protective circuit | ABB
10.6 | Incorporation of switching devices and components | Design rules | ASSEMBLY manufacturer must observe the original manufacturer´s instructions of the cabinet system and switching devices and components.
10.7 | Internal electrical circuits and connections | Design rules | The original parts/components must be assembled acc. to the original manufacturer´s instructions.
10.8 | Terminals for external conductors | Design rules | The original parts/components must be assembled according to the original manufacturer´s instructions.
10.9.2 | Dielectric properties Power-frequency withstand voltage | ABB
10.9.3 | Dielectric properties Impulse withstand voltage | ABB
10.10 | Verification of temperature rise | ABB | Please read for more information the devices catalogue and manual
10.11 | Short-circuit withstand strength | ABB
10.12 | Electromagnetic compatibility (EMC) | Not required | Applicability for environmental conditions "A" and "B"
10.13 | Mechanical operation | ABB
0